# INL1 -3: Impact of Supply System Selection

Abhijith Sivaprasadan

This assignment is intended to examine the impact of various supply units for heating and cooling in the built environment. The building is the same as in the previous assignment, as well as the simulation software (IDA ICE).

The impact of the different selections is to be evaluated in terms of bought energy, primary energy used, and environmental impact, for the building operating the entire year. You may, if you’d like to, do a cooling and heating design simulation in order to ensure sufficient capacity, as these are faster to run compared to an annual simulation. In the reference system heating is provided by the boiler inside the building and the fuel used is oil. The cooling required in the Air Handling Unit and the room cooling units are provided using a liquid chiller inside the building.

| Sl No: | Instructions | Bought Energy (KWh) | Primary Energy Used (KWh) | CO2 Emission (Kg) |
| --- | --- | --- | --- | --- |
| 1 | Reference System Boiler and Liquid Chiller | 111963 | 217524.1 | 41231.6 |
| 2 | Changing the compressor type of Brine to water chiller from reciprocating to “Screw” | Error | Error | Error |
| 3 | Changing the compressor type of Brine to water chiller from reciprocating to “turbo” with total cooling capacity of 40KW | 112908.2 | 219897.3 | 41629.7 |
| 4 | Changing the compressor type of Brine to water chiller from reciprocating to “turbo” with total cooling capacity of 50KW | 113319.4 | 220951.2 | 41804.8 |
| 5 | District heating and cooling | 148461 | 257040.8 | 47138.8 |
| 6 | Ground source heat pump and liquid chiller | 80407.3 | 196806 | 33063.4 |
| 7 | Changing the relative size of the auxiliary heating “Top-up heating” and the rating heating capacity of the brine heat pump, keeping the total heating capacity. Top up heating = 20KW Rated heating capacity = 10KW | 87717.4 | 187573.6 | 31512.3 |
| 8 | Changing the compressor type of Brine to water chiller from reciprocating to “turbo” with total cooling capacity of 40KW | 79814.2 | 198114.8 | 33283.2 |
| 9 | GSHP, liquid chiller, and PV-panels | -25818.9 | -68068.7 | -11435.5 |
| 10 | GSHP, liquid chiller, and PV-panels with half the area | 27287.3 | 64378 | 10815.5 |
| 11 | Air Source Heat Pump (ASHP) and liquid chiller | 83131.9 | 200319 | 33653.3 |

Findings

- When the compressor type of brine to water chiller was change from reciprocating to turbo, the bought energy, primary energy used and the CO2 emissions had an increase which could be due to the efficiency difference between the compressors. Generally reciprocating compressor would be more efficient than turbo compressors.

- There was an overall increase in bought energy, primary energy used and CO2 emission when the rated capacity of the total cooling was increased.

- After loading the “District heating and district cooling.idm” file was load and the simulated, there was a significant increase in all the parameters.

- After loading the “GSHP and Liquid chiller.idm” file and running the simulation, l the three measures in question decreased significantly compared to the reference system. This might be due to the fact that Ground source heat pump and liquid chiller system has a higher efficiency than the boiler and liquid chiller system.

- Changing the compressor type of Brine to water chiller from reciprocating to “turbo” with total cooling capacity at 40KW

- But when the top up heating was set to 5KW and rated capacity to 25KW, there was decrease in the bought energy whereas the emission and primary energy used decreased compared to the previous settings.

- When the PV panel was utilized in conjunction with the GSHP and liquid chiller system in the building, it fulfilled all of the energy requirements, and any excess energy generated could be sent back into the grid, resulting in negative bought energy, primary energy consumed, and carbon emissions.

- However, there was no extra energy created when the PV panel with half the area was used. There was also a greater demand for energy, which resulted in a positive emission and positive purchased energy.

- The ASHP with liquid chiller is more energy efficient and has a lower environmental effect than the reference system. It does, however, use more energy than the GSHP and liquid chiller systems.

Conclusion

The research shows that when energy efficient technologies are employed, the purchased energy and associated emissions are decreased. In this case, the emissions and purchased energies are lower for the GSHP and liquid chiller system than for the boiler and liquid chiller and ASHP and liquid chiller systems. Furthermore, when the PV panel was combined with the GSHP and liquid chiller system, there was excess energy that could be put back into the grid, lowering emissions.